## Sheet1
Treated Fresh Air Unit (TFA Unit)
Fault | Sr. No | Parameter | Possiblity | Suggestion
Mechanical / Electrical | 1 | Fan Failure | Supply fan not running | Power Supply Issue/ Unit in Manual Mode/ Damper Status Not received/ Unit Offline.
|  |  | Motor overload trip | Check Power Supply for Overload Current / Voltage.
|  |  | VFD fault (VFD Trip point) | Check for the alarm.
|  |  | Uncommanded fan stop | Power Supply Issue/Unit Offline.
| 2 | Damper Fault | Outdoor/return air damper stuck (not modulating as commanded) | Actuator Stuck/ Not properly installed/ Power Supply Issue/Actuator Faulty
|  |  | Feedback mismatch with command signal | Actuator Stuck/ Not properly installed.
|  |  | Actuator failure | Actuator Stuck/Power Supply Issue.
| 3 | Filter Choke Alarm | High differential pressure across filter | Clogged filters requiring cleaning or replacement
| 4 | Cooling Coil Faults | Valve actuator fault for chilled water coils | Power Supply Issue / Actuator Stuck
|  |  | Low or no temperature change across coil | Power Supply Issue / Faulty Sensor / Unit Not working.
Environmental and Sensor-Based Alarms | 1 | High/Low Supply Air Temperature | Deviates beyond configured setpoints | Potential ductwork leak or room conditions deviation
Coil Choke
| 2 | CO₂ High Alarm |  | Indicates poor ventilation or over-occupancy
Power and Communication Errors | 1 | Phase Loss / Power Failure | Power supply interruption to the TFA unit | Check Power Supply
BMS Communication Failure | 1 | Loss of communication with the TFA controller | Power supply interruption to the TFA Controller | Check Power Supply
| 2 | Data not updating in BMS | Network Issue/ System Offline | Check Network strength
Air Cooled Water Chillers
Fault | Sr. No | Parameter | Possiblity | Suggestion
Mechanical / Electrical | 1 | Compressor Fault | High discharge temperature | Alarms will be generated on the Chiller Controller
|  |  | Overload/overcurrent trip | Alarms will be generated on the Chiller Controller
|  |  | Short cycling (frequent start-stop) | Alarms will be generated on the Chiller Controller
|  |  | Locked rotor or no-start condition | Alarms will be generated on the Chiller Controller
|  |  | Unbalanced load (in multi-compressor systems) | Alarms will be generated on the Chiller Controller
| 2 | Condenser Fan Fault | Fan motor overload or trip | Alarms will be generated on the Chiller Controller
|  |  | VFD fault (if VFD-controlled fans) | Alarms will be generated on the Chiller Controller
|  |  | Fan not running when commanded | Alarms will be generated on the Chiller Controller
|  |  | High condensing pressure due to fan failure | Alarms will be generated on the Chiller Controller
| 3 | Refrigerant Circuit Fault | Low refrigerant pressure alarm | Alarms will be generated on the Chiller Controller
|  |  | High refrigerant pressure alarm | Alarms will be generated on the Chiller Controller
|  |  | Low suction temperature | Alarms will be generated on the Chiller Controller
|  |  | Refrigerant leak detected (if sensors available) | Alarms will be generated on the Chiller Controller
| 4 | Pump Related Faults (Secondary/Primary) | Pump not running
Low differential pressure
VFD fault (if present)
Motor overload
Temperature / Pressure-Based Alarms | 1 | High Chilled Water Supply Temperature | Indicates poor cooling performance or system overshoot
| 2 | Low Chilled Water Supply Temperature | Risk of coil freezing or load mismatch
| 3 | High Condenser Pressure | Poor heat rejection due to fouled coil or fan failure
| 4 | Low Evaporator Pressure | Possible refrigerant undercharge, flow issue, or sensor fault
| 5 | Entering/Leaving Chilled Water Temp Deviation | Excessive delta-T or insufficient delta-T alarm
Can indicate flow issues or heat exchanger fouling
Operational Errors / System Health |  | Chiller Not Available / Off | Due to local control, BMS disable signal, or fault lockout
| 1 | Frequent Compressor Starts | Indicates control loop instability or improper capacity control
| 2 | Flow Switch Trip (Low Water Flow) | Protects evaporator from freezing
Triggered due to pump failure, air lock, or closed valve
| 3 | Strainer Clogged (if DP sensor installed) | High pressure drop across strainer
| 4 | Low Ambient Lockout | Chiller disabled due to low outside temperature (based on OEM limits)
| 5 | Freeze Protection Alarm | Low temperature at evaporator or water circuit – risk of ice formation
Power and Communication Issues | 1 | Phase Loss / Phase Reversal | Protective trip to prevent motor damage
| 2 | Main Power Supply Failure | Total power loss to the chiller
BMS Communication Loss | 1 | Chiller controller not responding or offline
Pumps
Fault | Sr. No | Parameter | Possiblity | Suggestion
Mechanical / Electrical | 1 | On/Off Command | Command Not Working | Unit in Manual Mode / Unit Offline / Power Suppy Issue
| 2 | On/Off Status | Unit in manual mode/connection issue/system offline | Not properly installed/ Power Supply Issue
| 3 | Trip Status | Pump Fault (Trip status) | Check for the alarm.
Power and Communication Errors | 1 | Phase Loss / Power Failure | Power supply interruption to the Pump unit | Check Power Supply
BMS Communication Failure | 2 | Data not updating in BMS | Network Issue/ System Offline | Check Network strength
AQI Sensors
Fault | Sr. No | Parameter | Possiblity | Suggestion
Environmental and Sensor-Based Alarms | 1 | AQI | Range Between 0 - 50 | Good / Minimal Impact
|  |  | Range Between 51 - 100 | Satisfactory / Minor Breathing Discomfort To Sensitive People
|  |  | Range Between 101 - 200 | Moderate / Breathing Discomfort to the people with lungs, asthma & heart diseases
|  |  | Range Between 201 - 300 | Poor / Breathing Discomfort to most people on prolonged exposure
|  |  | Range Between 301 - 400 | Very Poor / Respiratory illness on prolonged exposure
|  |  | Range Between 401 - 500 | Severe / Affects Healthy People & Seriously impacts those with existing diseases
| 2 | CO2 | Range Between 400 - 800 | Acceptable conditions with normal level of CO2
|  |  | Range Between 801 - 1200 | Fair / Upper Limit of CO2 Concentration For Indoor Level
|  |  | Range Between 1201 -1800 | Poor / Complaints of Drowsiness and poor air, weak people could faint and cough
|  |  | Range Between 1801 - 2100 | Dangerous / Poor Concentration, Increased Heart Rate, Headaches, Sleepiness
| 3 | pm 10 | Range Between 0 - 50 | Good / Minimal Impact
|  |  | Range Between 51 - 100 | Satisfactory / Minor Breathing Discomfort To Sensitive People
|  |  | Range Between 101 - 250 | Moderate / Breathing Discomfort to the people with lungs, asthma & heart diseases
|  |  | Range Between 251 - 350 | Poor / Breathing Discomfort to most people on prolonged exposure
|  |  | Range Between 351 - 430 | Very Poor / Respiratory illness on prolonged exposure
|  |  | Range 430 + | Severe / Affects Healthy People & Seriously impacts those with existing diseases
| 4 | pm 2.5 | Range Between 0 - 30 | Good / Minimal Impact
|  |  | Range Between 31 - 60 | Satisfactory / Minor Breathing Discomfort To Sensitive People
|  |  | Range Between 61 - 90 | Moderate / Breathing Discomfort to the people with lungs, asthma & heart diseases
|  |  | Range Between 91 - 120 | Poor / Breathing Discomfort to most people on prolonged exposure
|  |  | Range Between 121 - 250 | Very Poor / Respiratory illness on prolonged exposure
|  |  | Range 250 + | Severe / Affects Healthy People & Seriously impacts those with existing diseases
| 5 | Battery | Battery Reaing > 2.7 | Good / Healthy Condition
|  |  | Battery Reading <= 2.7 | Battery Levels Dropping, Battery needs to be replaced
Power and Communication Errors | 1 | Battery Failure | Battery Burned Out | Check / Replace Battery
BMS Communication Failure | 2 | Data not updating in BMS | Network Issue/ System Offline | Check Network Strength

## Sheet3
Environmental and Sensor-Based Alarms
6. High/Low Supply Air Temperature
Deviates beyond configured setpoints
Indicates coil control issue or sensor fault
7. High/Low Return Air Temperature
Potential ductwork leak or room conditions deviation
8. Humidity Out of Range
If humidifier/dehumidifier is present
High RH = mold risk, Low RH = comfort issues
9. Airflow Failure
Low/no differential pressure across fan
Broken belt or fan blade issue
10. Outdoor Air Temperature Sensor Fault
Sensor value out of plausible range (e.g., -40°C or 100°C)
Open/short circuit detection
🦠 Air Quality Monitoring (if installed)
11. CO₂ High Alarm
Indicates poor ventilation or over-occupancy
12. VOC/PM Level Alarm
For spaces requiring air purity monitoring (labs, hospitals, etc.)
🔌 Power and Communication Errors
13. Phase Loss / Power Failure
Power supply interruption to the TFA unit
14. BMS Communication Failure
Loss of communication with the TFA controller
Data not updating in BMS
🧰 Optional/Advanced Alarms
15. Differential Pressure Sensor Fault
Faulty readings from DP sensors across filters/fans
16. Low Water Flow (for coil-fed systems)
Chilled/hot water flow below threshold
Indicates valve blockage or pump issue
17. Unscheduled Operation
Unit running outside programmed time schedule
18. Access Panel Open (if door switch present)
Security or safety alert for unauthorized access
19. Fire Alarm Interlock Active
Shutdown triggered via fire alarm interface

## Sheet4
🔧 Mechanical / Electrical Faults
1. Compressor Fault
High discharge temperature
Overload/overcurrent trip
Short cycling (frequent start-stop)
Locked rotor or no-start condition
Unbalanced load (in multi-compressor systems)
2. Condenser Fan Fault
Fan motor overload or trip
VFD fault (if VFD-controlled fans)
Fan not running when commanded
High condensing pressure due to fan failure
3. Refrigerant Circuit Fault
Low refrigerant pressure alarm
High refrigerant pressure alarm
Low suction temperature
Refrigerant leak detected (if sensors available)
4. Pump Related Faults (Secondary/Primary)
Pump not running
Low differential pressure
VFD fault (if present)
Motor overload
🌡️ Temperature / Pressure-Based Alarms
5. High Chilled Water Supply Temperature
Indicates poor cooling performance or system overshoot
6. Low Chilled Water Supply Temperature
Risk of coil freezing or load mismatch
7. High Condenser Pressure
Poor heat rejection due to fouled coil or fan failure
8. Low Evaporator Pressure
Possible refrigerant undercharge, flow issue, or sensor fault
9. Entering/Leaving Chilled Water Temp Deviation
Excessive delta-T or insufficient delta-T alarm
Can indicate flow issues or heat exchanger fouling
🛠️ Operational Errors / System Health
10. Chiller Not Available / Off
Due to local control, BMS disable signal, or fault lockout
11. Frequent Compressor Starts
Indicates control loop instability or improper capacity control
12. Flow Switch Trip (Low Water Flow)
Protects evaporator from freezing
Triggered due to pump failure, air lock, or closed valve
13. Strainer Clogged (if DP sensor installed)
High pressure drop across strainer
14. Low Ambient Lockout
Chiller disabled due to low outside temperature (based on OEM limits)
15. Freeze Protection Alarm
Low temperature at evaporator or water circuit – risk of ice formation
🔌 Power and Communication Issues
16. Phase Loss / Phase Reversal
Protective trip to prevent motor damage
17. Main Power Supply Failure
Total power loss to the chiller
18. BMS Communication Loss
Chiller controller not responding or offline
📊 Sensor Faults & Calibration
19. Temperature Sensor Fault
Open/short sensor
Implausible readings (e.g. -40°C, +150°C)
20. Pressure Sensor Fault
Sensor failure or value out of range
🔒 Safety Interlocks and External Inputs
21. Emergency Stop Activated
Manual or external safety trigger engaged
22. Fire Alarm Interlock
Chiller shutdown initiated via fire signal
23. Remote Stop/Start Interlock
Overriding local control via external command
📑 Optional/Advanced Monitoring (if available)
24. Oil Pressure Loss (for screw compressors)
Alarm for low oil pressure differential
25. Expansion Valve Error (EEV/TXV)
Feedback error or valve stuck
26. High Vibration Alarm (if sensor installed)
Mechanical wear or impending failure
27. Condenser Coil Temperature Differential
Fouling or poor airflow detection